LINE CONSTANTS AND LINE PARAMETER FILES

───────────────────────────────────────

│─────────68.8'───────│

│─21.0'─│

─┬─     │       o 	   	    o

#7               #8

28.0'    │

1.5|        #2      #5

─┴─     o  o           o  o           o  o

│     #│1   #4                    #3      #6

│

│      │───── 45.0'───│

│

│      │─────────── 90.0' ───────────│

122'tower   │

(85'mspan)

│

│

│      │

───────────────────────────────────────────────

///////////////////////////////////////////////

TC - 1

Input File (Mlin.dat) for LINDA Runs

8,100,60,0,0

.0511,.349,1.75,122.0,00.0,85.,0,0

.0511,.349,1.75,122.0,45.0,85.,0,0

.0511,.349,1.75,122.0,90.0,85.,0,0

.0511,.349,1.75,122.0,01.5,85.,1,0

.0511,.349,1.75,122.0,46.5,85.,2,0

.0511,.349,1.75,122.0,91.5,85.,3,0

2.44,.749,.385,160.0,45.0,113.0,0,1

2.44,.749,.385,160.0,90.0,113.0,0,1

▐       146 mi          ▌

▐─────────────────┬─────▌

▐                 │     ▌

▐                 3     ▌

▐                 │     ▌

▐                -╧-    ▌

▐       146 mi          ▌

▐─────────────────┬─────▌

▐                 │     ▌

▐                 3     ▌

│

S23               -╧-    S12

Doble Circuit Line Cross Section Geometry

CKT #2                                            CKT #1

│────────────────────────────────  285.8' ─────────────────────────────────│

│────────────────────────────  236.5'──────────────────────│

│──────────  68.8'───────│

│─19.5'─│

─┬─   │  	  o 		   o 		               	     o       	     o

#13              #14                               #15             #16

35.75' │

1.5|        #6      #12                         #2      #8                     #1    #7

─┴─   o  o           o  o           o  o                 o  o           o  o           o  o

│    │5   #11                   #4      #10            #3      #9

│                │      │───── 43.4'───│

│

│      │─────────── 86.8' ───────────│

120' tower   │──────────────────────  217'──────────────────────│

(90' mspan)   ──────────────────────────────── 260.4'──────────────────────────│

│───────────────────────────────────────── 303.8'───────────────────────────────│

│                     │────────────────── 217'───────────────────────────│

│      │

──────────────────────────────────────────────────────────────────────────────────────────────

//////////////////////////////////////////////////////////////////////////////////////////////

Input File (MLIN.DAT) to LINDA Program

2,2

16,100,60,0,0

.0511,.349,1.75,120,303.8,90,0,0

.0511,.349,1.75,120,217.0,90,0,0

.0511,.349,1.75,120,260.4,90,0,0

.0511,.349,1.75,120,086.8,90,0,0

.0511,.349,1.75,120,000.0,90,0,0

.0511,.349,1.75,120,043.4,90,0,0

.0511,.349,1.75,120,305.3,90,1,0

.0511,.349,1.75,120,218.5,90,2,0

.0511,.349,1.75,120,261.9,90,3,0

.0511,.349,1.75,120,088.3,90,4,0

.0511,.349,1.75,120,001.5,90,5,0

.0511,.349,1.75,120,044.9,90,6,0

2.44,.749,.385,155.75,019.5,125.75,0,1

2.44,.749,.385,155.75,068.8,125.75,0,1

2.44,.749,.385,155.75,236.5,125.75,0,1

2.44,.749,.385,155.75,285.8,125.75,0,1

TC - 3

LINDA  PROGRAM  Output  Files

FORT9  Output File

-----------------------------------------------------------------------------

LINE PARAMETER RUN, DATED                              1990/10/ 3     9:47 hr

-----------------------------------------------------------------------------

NUMBER  OF  COUPLED  THREE-PHASE  CIRCUITS            :          2

-----------------------------------------------------------------------------

NUMBER OF CONDUCTORS:16,FREQUENCY: 60.00 [Hz],EARTH RESISTIVITY: 100.00 [Ω-m]

-----------------------------------------------------------------------------

R [Ω/mi]      X [Ω/mi]       D [in]     HT [ft]    W [ft]  HM[ft]    C   GW

-----------------------------------------------------------------------------

0.0511        0.3490       1.75000     120.00    303.80    90.00    0    0

0.0511        0.3490       1.75000     120.00    217.00    90.00    0    0

0.0511        0.3490       1.75000     120.00    260.40    90.00    0    0

0.0511        0.3490       1.75000     120.00     86.80    90.00    0    0

0.0511        0.3490       1.75000     120.00      0.00    90.00    0    0

0.0511        0.3490       1.75000     120.00     43.40    90.00    0    0

0.0511        0.3490       1.75000     120.00    305.30    90.00    1    0

0.0511        0.3490       1.75000     120.00    218.50    90.00    2    0

0.0511        0.3490       1.75000     120.00    261.90    90.00    3    0

0.0511        0.3490       1.75000     120.00     88.30    90.00    4    0

0.0511        0.3490       1.75000     120.00      1.50    90.00    5    0

0.0511        0.3490       1.75000     120.00     44.90    90.00    6    0

2.4400        0.7490       0.38500     155.75     19.50   125.75    0    1

2.4400        0.7490       0.38500     155.75     68.80   125.75    0    1

2.4400        0.7490       0.38500     155.75    236.50   125.75    0    1

2.4400        0.7490       0.38500     155.75    285.80   125.75    0    1

-----------------------------------------------------------------------------

-----------------------------------------------------------------------------

CIRCUIT # 1  SYMMETRICAL  COMPONENT  PARAMETERS

-----------------------------------------------------------------------------

ZERO SEQUENCE SHUNT ADMITTANCE   [MHO/MILE]  POSITIVE SEQUENCE SHUNT ADMITTANCE

0.2437E-13    0.4344E-05                     -0.1282E-11    0.6744E-05

ZERO SEQUENCE SERIES IMPEDANCE    [Ω/MILE]   POSITIVE SEQUENCE SERIES IMPEDANCE

0.4947E+00    0.1584E+01                      0.2698E-01    0.6346E+00

----------------------------------------------------------------------------

----------------------------------------------------------------------------

CIRCUIT # 2  SYMMETRICAL  COMPONENT  PARAMETERS

----------------------------------------------------------------------------

ZERO SEQUENCE SHUNT ADMITTANCE   [MHO/MILE]  POSITIVE SEQUENCE SHUNT ADMITTANCE

0.2746E-13    0.4344E-05                     -0.1281E-11    0.6744E-05

ZERO SEQUENCE SERIES IMPEDANCE    [Ω/MILE]   POSITIVE SEQUENCE SERIES IMPEDANCE

0.4947E+00    0.1584E+01                      0.2698E-01    0.6346E+00

----------------------------------------------------------------------------

CIRCUIT #  1-TO-CIRCUIT #  2   SHUNT ADMITTANCES  [ Electrostatic  Coupling ]

----------------------------------------------------------------------------

ZERO SEQUENCE              [MHO/MILE]             POSITIVE SEQUENCE

-0.6305E-14   -0.2673E-06                        -0.2988E-07    0.4059E-07

-----------------------------------------------------------------------------

CIRCUIT #  1-TO-CIRCUIT #  2   SERIES IMPEDANCES [ Electromagnetic Coupling ]

-----------------------------------------------------------------------------

ZERO SEQUENCE               [Ω/MILE]              POSITIVE SEQUENCE

0.4159E+00    0.4913E+00                        -0.1705E-02   -0.5469E-02

----------------------------------------------------------------------------

*END OF RUN***END OF RUN***END OF RUN***END OF RUN***END OF RUN***END OF RUN

----------------------------------------------------------------------------

Mlin.lis Output File to be renamed FORT22 for ACTIB runs

0.0000000000000000E+00 0.5841249905411500E-05

0.0000000000000000E+00-0.3489321601202686E-06

0.0000000000000000E+00-0.1031618868900403E-05

0.0000000000000000E+00-0.6813865760090320E-07

0.0000000000000000E+00-0.2805795436368424E-07

0.0000000000000000E+00-0.3441281354265468E-07

TC - 4

0.0000000000000000E+00-0.3489321601202686E-06

0.0000000000000000E+00 0.5879240012002454E-05

0.0000000000000000E+00-0.1018991235829356E-05

0.0000000000000000E+00-0.2908425410977450E-06

0.0000000000000000E+00-0.6813865760090314E-07

0.0000000000000000E+00-0.1140476604589882E-06

0.0000000000000000E+00-0.1031618868900403E-05

0.0000000000000000E+00-0.1018991235829356E-05

0.0000000000000000E+00 0.6111257132299608E-05

0.0000000000000000E+00-0.1140476604589881E-06

0.0000000000000000E+00-0.3441281354265474E-07

0.0000000000000000E+00-0.4987394227085549E-07

0.0000000000000000E+00-0.6813865760090320E-07

0.0000000000000000E+00-0.2908425410977450E-06

0.0000000000000000E+00-0.1140476604589881E-06

0.0000000000000000E+00 0.5879240012002455E-05

0.0000000000000000E+00-0.3489321601202686E-06

0.0000000000000000E+00-0.1018991235829356E-05

0.0000000000000000E+00-0.2805795436368424E-07

0.0000000000000000E+00-0.6813865760090314E-07

0.0000000000000000E+00-0.3441281354265474E-07

0.0000000000000000E+00-0.3489321601202686E-06

0.0000000000000000E+00 0.5841249905411498E-05

0.0000000000000000E+00-0.1031618868900404E-05

0.0000000000000000E+00-0.3441281354265468E-07

0.0000000000000000E+00-0.1140476604589882E-06

0.0000000000000000E+00-0.4987394227085549E-07

0.0000000000000000E+00-0.1018991235829356E-05

0.0000000000000000E+00-0.1031618868900404E-05

0.0000000000000000E+00 0.6111257132299606E-05

0.1772325835888922E+00 0.9617365092408162E+00

0.1520002615471881E+00 0.2647185016525417E+00

0.1565173879014271E+00 0.3457055910555138E+00

0.1375765923287089E+00 0.1629462360703778E+00

0.1296232207150336E+00 0.1323378323013610E+00

0.1347679868151939E+00 0.1423283081849883E+00

0.1520002615471881E+00 0.2647185016525417E+00

0.1829911706115235E+00 0.9477467688152313E+00

0.1591767591472528E+00 0.3387669613552587E+00

0.1458058374801300E+00 0.2144505237658507E+00

0.1375765923287089E+00 0.1629462360703778E+00

0.1435113825139327E+00 0.1806491968421112E+00

0.1565173879014271E+00 0.3457055910555138E+00

0.1591767591472528E+00 0.3387669613552587E+00

0.1884152209437560E+00 0.9433886102660739E+00

0.1435113825139327E+00 0.1806491968421111E+00

0.1347679868151939E+00 0.1423283081849883E+00

0.1404629022931060E+00 0.1552015125662233E+00

0.1375765923287089E+00 0.1629462360703778E+00

0.1458058374801300E+00 0.2144505237658507E+00

0.1435113825139327E+00 0.1806491968421111E+00

0.1829911706115236E+00 0.9477467688152315E+00

0.1520002615471882E+00 0.2647185016525417E+00

0.1591767591472528E+00 0.3387669613552588E+00

0.1296232207150336E+00 0.1323378323013610E+00

0.1375765923287089E+00 0.1629462360703778E+00

0.1347679868151939E+00 0.1423283081849883E+00

0.1520002615471882E+00 0.2647185016525417E+00

0.1772325835888924E+00 0.9617365092408164E+00

0.1565173879014272E+00 0.3457055910555143E+00

0.1347679868151939E+00 0.1423283081849883E+00

0.1435113825139327E+00 0.1806491968421112E+00

0.1404629022931060E+00 0.1552015125662233E+00

0.1591767591472528E+00 0.3387669613552588E+00

0.1565173879014272E+00 0.3457055910555143E+00

0.1884152209437561E+00 0.9433886102660745E+00

LINE DESCRIPTIONAL FILES

────────────────────────

S12                            S10

▌ ┌─┐  68 Ω      152 mi       ▌

─▌─│A│──) (───────────────┬────▌

▌ └─┘                    │    ▌

3

│

-╧-

TC - 5

FORT1 FILE

1

1,1

1,-19

152.

2

1.

1.

0.

0.               -600.

0.               -68.0

0.

0.

1

000

99999.

10

1.5,1.5

200.

▐       146 mi          ▌

▐─────────────────┬─────▌

▐                 │     ▌

▐        6OO µmho 3     ▌

▐                 │     ▌

▐                -╧-    ▌

▐       146 mi          ▌

▐─────────────────┬─────▌

▐                 │     ▌

▐        6OO µmho 3     ▌

│

S23               -╧-    S12

FORT2 FILE

2

2,2

1,2

146.

2

1.

1.

1.

1.

0.

0.               -600.

0.

0.               -600.

0.

0.

0.

0.

SUBSTATION FILES

────────────────

FORT10 FILE

0,0,0

FORT12 FILE

0,1,0

300.,300.,50.,0,0.

(200.,50.)

500.,132.,13.2

(0.,0.05),(0.,2.24),(0.,.38)

FORT23 FILE

0,0,0

TC - 6

TEST SYSTEM # 1

───────────────

One line diagram

────────────────

┌─────────────────────────────┐

│─────────────────────┤     Ztransfer=32+j130 Ω     │────────────────│

└─────────────────────────────┘

Zo=3.05+j40.7  Ω

Z1=1.56+j16.21 Ω

500 KV ▐ a     146 mi          ▌ 500 KV                                                 ┌───┐

▐─o───────────────┬─────▌                                           S10   ┌──────┤ S │

▐                 │     ▌      S12                                        │      └───┘

┌───┐         ▐        6OO µmho 3     ▌                ▌ ┌─┐  68Ω       152 mi     ▌    │

│ S ├─────────▐                 │     ▌───────┬────────▌─│A│──) (──────────────┬───▌────┴───────┐

└───┘         ▐                -╧-    ▌       │        ▌ └─┘                   │   ▌           ┌┴┐

Z1=2.68+j46.19 Ω ▐       146 mi        b ▌       │                                3               │ │ 502-j

Zo=5.00+j86.80 Ω ▐─────────────────┬───o─▌       3                       6OOµmho  │               └┬┘ 50 MVA

▐                 │     ▌       3───┐                           -╧-              -╧-

▐                 3     ▌       3  ┌┴┐

6OOµmho │             │  │ │ 2OO+j5O MVA

S23               -╧-            │  └┬┘

-╧- -╧-

VOLTAGE SOURCE AND OVERALL NETWORK DATA FILE   (FORT8 Input File for ACTIB Runs)

────────────────────────────────────────────

Test System # 1

for ACTIB Runs

1,2

500.

2.68            46.19

5.00            86.8

1.56            16.21

3.05            40.7

32.0		130.0

-100.

400.

50.

102.

SUMMARY OF DATA FILES FOR ACTIB RUNS

────────────────────────────────────

FORT1       module 1 descriptional file

FORT11      module 1 line  constants file

FORT2       module 2 descriptional file

FORT22      module 2 line  constants file

FORT10      substation 10 file

FORT12      substation 12 file

FORT23      substation 23 file

FORT8       voltage source and overall network data file

TEST CASES

──────────

Case #1 :  A  2Ω  SLGF is applied in phase 2 at 3.42 miles from substation 10  on the 152-mile line.

───────

Ground current and changes from the unfaulted system as seen at location  'a' in  S23

are required.   Also the series capacitor variables including MOV 1-second energy.

TC - 7

C:>R1

*    ╔═══════════════════════════════════════════════╦════════════════════╗

*    │   A C T I B   Base Case  run  in  progress    ║                    │

*    │     (C) Copyright  Alberto Ramirez 1991       ║   1992/4/4   17:10 │                                │

*    │      Version # -  All rights reserved.        ║                    │

*    ╚═══════════════════════════════════════════════╩════════════════════╝

*	  ENTER  1  FOR SERIES PROBE ACTIVATION IN INTERACTIVE MODE   -> 1

*     ──────────────────────────────────────────────────────────────────────────

*                      I N I T I A L    L O A D    F L O W

*     ──────────────────────────────────────────────────────────────────────────

*                                       288.8(φ  -8.5)         276.3(φ -11.8)

*                                             ▐                       ▌

*                                             ▐P->  375.2   P->  372.6▌

*                                             ▐───────────────────────▌

*                                             ▐Q-> -178.8   Q->  -93.8▌

*                                             ▐                       ▌

*

*              290.3(φ  -6.0)          288.8(φ  -8.5)

*                      ▐                       ▌

*                      ▐P->  287.4   P->  286.3▌

*                      ▐───────────────────────▌

*                      ▐Q->  -51.8   Q->  -62.3▌

*                      ▐                       ▌

*                      ▐                       ▌

*                      ▐P->  286.4   P->  284.8▌

*                      ▐───────────────────────▌

*                      ▐Q->  -50.1   Q->  -60.5▌

*                      ▐                       ▌

*

*

*       Execution terminated: ALF and FORT1OO base-case files created

C:>TYPE ALF

╔═════════════════════════════════════════════════════════════════════════════╗

│    A L F    F I L E                                  1992/ 4/ 4    17:10 hr │

╚═════════════════════════════════════════════════════════════════════════════╝

Test System # 1

for ACTIB Runs

─────────────────────────────────────────────────────────────────────────────

G E N E R A L   I N P U T         D A T A

─────────────────────────────────────────────────────────────────────────────

NUMBER OF NETWORKS    :      1      NUMBER OF LINE MODULES   :      2

─────────────────────────────────────────────────────────────────────────────

────────────────────────────

NETWORK #               1

────────────────────────────

BASE VOLTAGE :                                 500.00 [KV]

SENDING END SOURCE        Z1:        2.68  +j        46.19  [Ω]

SENDING END SOURCE        Z0:        5.00  +j        86.80  [Ω]

RECEIVING END  SOURCE     Z1:        1.56  +j        16.21  [Ω]

RECEIVING END  SOURCE     Z0:        3.05  +j        40.70  [Ω]

NET RECEIVING END LOAD      :      400.00  +j      -100.00  [MVA]

SCHEDULED  RECEIVING  END

GENERATOR  POWER            :      102.00  +j        50.00  [MVA]

------------------------------------------------------------------------------

LINE MODULE 1 INPUT DATA

------------------------------------------------------------------------------

NUMBER OF SECTIONS       :      1

LENGTHS OF SECTIONS [km] :    152.00

NUMBER OF 'PI' SECTIONS  :      2

SHUNT ELEMENT ADMITTANCE  [µMHO]

CKT#1                         ▐-SE─┬───────────┬─RE-▌

│           │

0.00  -j      0.00        3           3         0.00  -j    600.00

│           │

-╧-         -╧-

SERIES ELEMENT IMPEDANCE  [ Ω ]

CKT#1    0.00  -j     68.00   ▐-SE-)(---------)(-RE-▌    0.00  -j      0.00

TC - 8

SERIES COMPENSATION PROTECTION THRESHOLDS

CKT#1           ▐------)(-----│--------------------------------▌

▐     __      │

▐    /        │

`--[/]----> <-'

__/   Gset=  1.50 KA

Vo  │      o --            Vo =  200.00 KV peak

VARISTOR                      │    /

│  /

CHARACTERISTIC                └───────────────

i peak

-------------------------------------------

S E R I E S   P R O B E   A C T I V A T E D

-------------------------------------------

Location :  Sending End Bus of Line Module      ▐--##---------------▌

Circuit Phase Impedances [ Ω ] :

.------------------------------.

phase 1   ▐------│  0.000000E+00+j 0.000000E+00 │-----▌

`------------------------------'

.------------------------------.

CKT# 1             phase 2   ▐------│  0.000000E+00+j 0.000000E+00 │-----▌

`------------------------------'

.------------------------------.

phase 3   ▐------│  0.000000E+00+j 0.000000E+00 │-----▌

`------------------------------'

------------------------------------------------------------------------------

NETWORK#1 SUBSTATION 12 LOCAL TRANSFORMER

------------------------------------------------------------------------------

Nameplate MVA: Network#1 / Secondary / Tertiary          300.0 / 300.0 /  50.0

Nameplate KV : Network#1 / Secondary / Tertiary          500.0 / 132.0 /  13.2

Leakage Impedances in [pu] on Secondary MVA base

Network#1-Secondary                                  0.000E+00  0.500E-01

Network#1-Tertiary                                   0.000E+00  0.224E+01

Secondary-Tertiary                                   0.000E+00  0.380E+00

Secondary load [MW,MVAR]                                200.0 MW     50.0 MVAR

------------------------------------------------------------------------------

LINE MODULE 2 INPUT DATA

------------------------------------------------------------------------------

NUMBER OF SECTIONS       :      1

LENGTHS OF SECTIONS [km] :    146.00

NUMBER OF 'PI' SECTIONS  :      2

SHUNT ELEMENT ADMITTANCE  [µMHO]

CKT#1                         ▐-SE─┬───────────┬─RE-▌

│           │

0.00  -j      0.00        3           3         0.00  -j    600.00

│           │

-╧-         -╧-

CKT#2                         ▐-SE─┬───────────┬─RE-▌

│           │

0.00  -j      0.00        3           3         0.00  -j    600.00

│           │

-╧-         -╧-

SERIES ELEMENT IMPEDANCE  [ Ω ]

CKT#1    0.00  -j      0.00   ▐-SE-)(---------)(-RE-▌    0.00  -j      0.00

CKT#2    0.00  -j      0.00   ▐-SE-)(---------)(-RE-▌    0.00  -j      0.00

──────────────────────────────────────────────────────────────────────────────

I N I T I A L    L O A D    F L O W

──────────────────────────────────────────────────────────────────────────────

288.8(φ  -8.5)         276.3(φ -11.8)

▐                       ▌

▐P->  375.2   P->  372.6▌

▐───────────────────────▌

▐Q-> -178.8   Q->  -93.8▌

▐                       ▌

290.3(φ  -6.0)          288.8(φ  -8.5)

▐                       ▌

▐P->  287.4   P->  286.3▌

▐───────────────────────▌

▐Q->  -51.8   Q->  -62.3▌

▐                       ▌

▐                       ▌

▐P->  286.4   P->  284.8▌

▐───────────────────────▌

▐Q->  -50.1   Q->  -60.5▌

TC - 9

╔═══════════════════════════════════════════════╦════════════════════╗

│       A C T I B   run   in   progress         ║                    │

│     (C) Copyright  Alberto Ramirez 1991       ║      date   time   │                                │

│       Version # -  All rights reserved.       ║                    │

╚═══════════════════════════════════════════════╩════════════════════╝

Base Case of Reference                      1992/4/4    17:10

ENTER LINE MODULE TO BE FAULTED [1, OR 2]    OR ENTER 0 TO QUIT -> 1

┌───────────────────┐

│ FAULTED MODULE #1 │

└───────────────────┘

ENTER FAULT DISTANCE TO RECEIVING END [mi]  -> 3.42

-------------------------------------

S E R I E S   P R O B E   U P D A T E

-------------------------------------

Location :  Sending End Bus of Line Module #    ▐--##---------------▌

Circuit Phase Impedances [ Ω ] :

.------------------------------.

phase 1   ▐------│  0.000000E+00+j 0.000000E+00 │-----▌

`------------------------------'

.------------------------------.

CKT#         phase 2   ▐------│  0.000000E+00+j 0.000000E+00 │-----▌

`------------------------------'

.------------------------------.

phase 3   ▐------│  0.000000E+00+j 0.000000E+00 │-----▌

`------------------------------'

ENTER  1  FOR PROBE CHANGES IN THIS CIRCUIT -> 0

┌────────────────────────────────────────────┐

│ FAULT CONDITION AT 3.42 [mi] FROM  REC END │

└────────────────────────────────────────────┘

ENTER GROUNDED PHASE(1,2,OR 3)   OR   ENTER O FOR UNGROUNDED FAULT ->2

ENTER NUMBER OF PHASES TO GROUND ->1

ENTER PROBE ADMITTANCE  [ MHO ]  ->(0.5,0.0)

┌──────────────┐

│  MODULE # 1  │

└──────────────┘

.-------------------------------------------------------.

| SENDING END | CKT#1 | SERIES CAPACITOR CURRENTS  [KA] |

|-------------------------------------------------------|

|     0.57774E+00       0.15924E+01       0.37814E+00   |

|       φ    8.3          φ  179.5          φ  127.0    |

|-------------------------------------------------------|

|       39.3 KV           101.0 KV          25.7 KV     |

|-------------------------------------------------------|

|        0.0 MJ            57.9 MJ           0.0 MJ     |

|-------------------------------------------------------|

|     --)    (--        --) -> (--        --)    (--    |

`-------------------------------------------------------'

┌─────────────┬──────────────────────────────────────────────┐

│ C A S E   1 │       O U T P U T    S E L E C T I O N       │

└─────────────┴──────────────────────────────────────────────┘

ENTER : 5 TO SKIP OUTPUT COMPLETELY

OR   : LINE MODULE NUMBER FOR RESULTS OR : 0(ZERO) FOR ALL MODULES -> 2

ENTER : 0 FOR VALUES ON BOTH (SE) AND (RE) SIDES

: 1 FOR (SE) SIDE ONLY           OR : 2 FOR (RE) SIDE ONLY -> 1

ENTER : 0 FOR VALUES IN ALL CIRCUITS   OR :   CIRCUIT  NUMBER    -> 1

ENTER : 1 FOR ^V, ^I, AND GROUND CURRENTS

: 2 FOR APPARENT  Z AND Y AS SEEN AT RELAY  LOCATIONS      -> 1

----------------------------------------------------

------------------MODULE 2 RESULTS------------------

----------------------------------------------------

CKT#1 SENDING END VOLTAGES [KV]

0.29066E+03       0.21138E+03       0.29604E+03

φ   -4.9          φ  228.9          φ  113.2

CKT#1 SEND END ^U in [PU] from BASE CASE

0.18958E-01       0.28378E+00       0.21341E-01

φ  266.3          φ   12.7          φ  152.1

TC - 10

CKT#1 SENDING END CURRENTS [KA]

0.33057E+00       0.80470E+00       0.25826E+00

φ   -4.6          φ  185.0          φ  107.1

CKT#1 SEND END ^I in [KA] from BASE CASE                     Ground Current [KA

0.31173E-01       0.73459E+00       0.12499E+00

φ  140.7          φ   88.6          φ   32.0

0.56836E+00

----------------------------------------------------

---------------END OF MODULE 2 RESULTS--------------

---------------------------------------------------- ENTER 1 FOR SERIES PROBE

RESULTS -> 1

MODULE 1            │<-  Vdrop       0.000 (  0.0°) ->│    CKT# 1

301.668 ( -4.3°) ▐── i -->   0.578 (  8.3°) ────────▌ 301.668 ( -4.3°)

│<-  Vdrop       0.000 (  0.0°) ->│

156.482 (220.9°) ▐── i -->   1.592 (179.5°) ────────▌ 156.482 (220.9°)

│<-  Vdrop       0.000 (  0.0°) ->│

303.338 (106.9°) ▐── i -->   0.378 (127.0°) ────────▌ 303.338 (106.9°)

ENTER 1 FOR  INFORMATION AT FAULT LOCATION POINT -> 1

P   220.620 (-13.2°)                         3.111 ( 84.3°)

N    58.212 (-67.5°)                         3.230 (212.1°)

Z   156.943 ( 52.6°)                         3.401 (-27.6°)

333.110 (  3.5°)

0.618 (-18.6°) ─────>───┬────────>   0.618 (-18.6°)

│

v

0.000 (  0.0°)

22.579 (153.7°)

┌───────┐    1.728 ( 176.6°) ─────>───┬────────>   9.722 ( -30.3°)

│ CKT 1 │                             │

└───────┘                             v

11.289 (153.7°)

344.402 ( 94.3°)

0.375 ( 80.8°) ─────>───┬────────>   0.375 ( 80.8°)

│

v

0.000 (  0.0°)

P     0.859 (-50.1°)                                 3.763 (-86.3°)

N     0.542 ( 43.2°)                                 3.763 ( 33.7°)

Z     0.371 (165.7°)                                 3.763 (153.7°)

────────────────────────────────────────────────────

---------- END OF RESULTS AT FAULT POINT -----------

──────────────────────────────────────────────────── ENTER 1 FOR DOCUMENTATION

OF THIS CASE -> 1

┌─────────────────────────────────────────────────────────────────────────────┐

│           E N D     O F     C A S E     1                                   │

└─────────────────────────────────────────────────────────────────────────────┘

ENTER LINE MODULE TO BE FAULTED [1, OR 2]    OR ENTER 0 TO QUIT -> 1

@	Case #2 :  An ungrounded DLGF  (phases 2 and 3) is applied at  120  miles from  substation 10 on

@      ───────

@	   the 152-mile line of Test System # 1.  A single-phase (phase 2) stuck-pole  condition

@

@	   is assumed in breaker A.   The MOV energy dissipated in one second  plus the  apparent

@

@          Z  and  Y  as  seen  from  relays  in  'b' location are required.

┌──────────────────┐

│ FAULTED MODULE #1│

└──────────────────┘

ENTER FAULT DISTANCE TO RECEIVING END [mi]  -> 120

-------------------------------------

S E R I E S   P R O B E   U P D A T E

-------------------------------------

Location :  Sending End Bus of Line Module #    ▐--##---------------▌

TC - 11

Circuit Phase Impedances [ Ω ] :

.------------------------------.

phase 1   ▐------│  0.000000E+00+j 0.000000E+00 │-----▌

`------------------------------'

.------------------------------.

CKT#         phase 2   ▐------│  0.000000E+00+j 0.000000E+00 │-----▌

`------------------------------'

.------------------------------.

phase 3   ▐------│  0.000000E+00+j 0.000000E+00 │-----▌

`------------------------------'

ENTER  1  FOR PROBE CHANGES IN THIS CIRCUIT -> 1

ENTER PHASE CODE FOR ALTERNATE IMPEDANCE APPLICATION

: 0 FOR NO CHANGE, AS  PROMPTED BELOW

: 1 FOR CHANGE

φφφ

###

123

010   (<--- CODE ENTERED BY USER)

┌───────────────────────────────────────────┐

│ FAULT CONDITION AT 120 [mi] FROM  REC END │

└───────────────────────────────────────────┘

ENTER GROUNDED PHASE(1,2,OR 3)   OR  ENTER O FOR UNGROUNDED FAULT -> 0

ENTER UNFAULTED PHASE (1,2 OR 3) OR 0 FOR 3-PHASE UNGRDED FAULT -> 1

ENTER A NON-ZERO UNGROUNDED FAULT ADMITTANCE [ MHO ] -> (0.5,0.0)

┌──────────────┐

*  *  *  *  * │  MODULE # 1  │ *  *  *  *  *  *  *  *  *  *  *  *  *  *  *  * *

└──────────────┘

.-------------------------------------------------------.

| SENDING END | CKT#1 | SERIES CAPACITOR CURRENTS  [KA] |

|-------------------------------------------------------|

|     0.12955E+00       0.30881E-01       0.30777E+01   |

|       φ  192.7          φ  260.8          φ   63.1    |

|-------------------------------------------------------|

|        8.8 KV             2.1 KV         167.8 KV     |

|-------------------------------------------------------|

|        0.0 MJ             0.0 MJ         308.7 MJ     |

|-------------------------------------------------------|

|     --)    (--        --)    (--        --) -> (--    |

`-------------------------------------------------------'

┌─────────────┬──────────────────────────────────────────────┐

│ C A S E   # │       O U T P U T    S E L E C T I O N       │

└─────────────┴──────────────────────────────────────────────┘

ENTER : 5 TO SKIP OUTPUT COMPLETELY

OR   : LINE MODULE NUMBER FOR RESULTS OR : 0(ZERO) FOR ALL MODULES -> 2

ENTER : 0 FOR VALUES ON BOTH (SE) AND (RE) SIDES

: 1 FOR (SE) SIDE ONLY           OR : 2 FOR (RE) SIDE ONLY ->  2

ENTER : 0 FOR VALUES IN ALL CIRCUITS   OR :   CIRCUIT  NUMBER    ->  2

ENTER : 1 FOR ^V, ^I, AND GROUND CURRENTS

: 2 FOR APPARENT  Z AND Y AS SEEN AT RELAY  LOCATIONS      ->  2

----------------------------------------------------

------------------MODULE 2 RESULTS------------------

----------------------------------------------------

CKT#2 RECEIVING END VOLTAGES [KV]

0.34772E+03       0.30196E+03       0.12965E+03

φ  -10.1          φ  252.3          φ   40.4

CKT#2 REC END APPARENT Z [ohm]

0.38246E+04       0.54173E+04       0.84776E+02

φ  238.0          φ  -71.6          φ  156.9

CKT#2 RECEIVING END CURRENTS [KA]

0.90915E-01       0.55740E-01       0.15293E+01

φ  -68.1          φ  143.9          φ   63.5

CKT#2 REC END APPARENT Y [mho]

0.26146E-03       0.18459E-03       0.11796E-01

φ  122.0          φ   71.6          φ  203.1

----------------------------------------------------

---------------END OF MODULE 2 RESULTS--------------

---------------------------------------------------- ENTER 1 FOR SERIES

TC - 12

PROBE RESULTS

MODULE 1            │<-  Vdrop       0.000 (  0.0°) ->│    CKT# 1

347.718 (-10.1°) ▐── i -->   0.130 (192.7°) ────────▌ 347.718 (-10.1°)

│<-  Vdrop     308.781 (260.8°) ->│

301.961 (252.3°) ▐── i -->   0.031 (260.8°) ────────▌  45.743 (158.0°)

│<-  Vdrop       0.000 (  0.0°) ->│

129.649 ( 40.4°) ▐── i -->   3.078 ( 63.1°) ────────▌ 129.649 ( 40.4°)

ENTER 1 FOR INFORMATION AT FAULT POINT -> 1

P   129.179 (-16.0°)                         1.728 ( 85.9°)

N   120.877 ( -9.6°)                         1.363 (260.4°)

Z   124.252 (-16.8°)                         0.472 (265.1°)

373.720 (-14.2°)

0.170 (213.8°) ─────>───┬────────>   0.170 (212.0°)

│

v

0.005 (-57.9°)

20.400 (217.5°)

┌───────┐    0.014 ( 259.4°) ─────>───┬────────>   2.838 ( -19.9°)

│ CKT 1 │                             │

└───────┘                             v

2.836 (160.4°)

11.334 (-19.6°)

3.088 ( 63.0°) ─────>───┬────────>   2.668 (187.7°)

│

v

5.100 ( 37.5°)

P     1.032 (-59.9°)                                 2.646 (-81.4°)

N     1.082 (184.4°)                                 1.520 (124.0°)

Z     0.976 ( 64.6°)                                 1.427 ( 71.3°)

────────────────────────────────────────────────────

---------- END OF RESULTS AT FAULT POINT -----------

──────────────────────────────────────────────────── ENTER 1 FOR DOCUMENTATION

OF THIS CASE -> 0

┌─────────────────────────────────────────────────────────────────────────────┐

│           E N D     O F     C A S E     2                                   │

└─────────────────────────────────────────────────────────────────────────────┘

ENTER LINE MODULE TO BE FAULTED [1, OR 2]    OR ENTER 0 TO QUIT -> 0

------------------------------------------------------------------------------

**END OF RUN**END OF RUN**END OF RUN**END OF RUN**END  OF RUN**END OF RUN**END

------------------------------------------------------------------------------

TC - 13